## RTU_CONV_SS_BOM
Annexure- I (Schedule of Items)- FY 26 & FY 27
Sl. No. | Item Description | Description | UOM | Per Sub-Station | TPCODL | TPNODL | TPWODL | Total Required Quantity (A) | Unit Rate (B) | GST (%) | GST (INR) (C) | Gross Unit Rate (D=B+C) | Gross Price (E=A*D) | Remarks
A | Supply Items
1a | Pre-Wired RTU Panel | Pre-Wired RTU Panel I/O Requirement: with 16 DI, 8 DO, 4 AI with Auxiliary relay for each Digital Input & Output Communication Ports per RTU :2x Redundant Ethernet ports; 2 Nos. Ethernet ports/Processor Module ( Both Ethernet Port for simultaneous communication with Control Centre SCADA over IEC60870-5-104 Protocol and IEDs in the Substation over IEC61850 and Modbus TCP Protocol), 4 Nos. Redeundant RS 485 ports/Processor Module for communication with serial devices over IEC60870-5-103, MODBUS (Serial) and IEC 60870-5-101 protocol with the RTU. Power supply: Redundant 18-72 VDC (24 V/48 V DC) Power Supply and Diode Oring unit and MCBs with add-on NO contact SPD: 4 Nos. SPD for RS485 Ports & 4 Nos. SPD for Ethernet port Protocols : IEC 60870-5-104, IEC 61850 (ED1, ED2), IEC 60870-5-101, IEC60870-5-103, MODBUS (Serial & TCP/IP), SNMP (V1.0, V2.0, V3.0), RSTP, NTP & SNTP, Software Licenses: RTU OS, Application Software, Configuration tools, Diagnostic tools. Logic building Application-Interlock logic, Calculation Package, SMS Utility Software Application Software Licenses with minimum 5000 Data Points, 25 IEDs - IEC61850 (ED1, ED2), 20 IEDs - Serial Protocol, RTU shall Communicate to Eight Independent Remote SCADA Master on IEC 60870-5-104 Mounting: To be supplied with prewired panel (Rittal/Siemens or equivalent, size : 2315 (H) mm x 800(W) mm x 800(D) mm, both side opening), IP Class : IP54/55. Other Accessories: Interface Modules, Pre-fabricated cables for I/O modules, Auxiliaries Relays for Power Supply monitoring, MCBs for all type of Power Supplies, Networking accessories: All required networking accessories like Patch cords (UTP as per the Ethernet Switch Configuration) of suitable length, Conduits for all non-armored cables, RJ45 connectors, I/O boxes with Quad face plate and connectors etc. | EA | 1 Nos. | 0 | 46 | 0 | 46 |  | 18% | 0 | 0 | 0
1b | Pre-Wired RTU Panel | Pre-Wired RTU Panel Communication Ports per RTU :4x Redundant Ethernet ports; 4 Nos. Ethernet ports/Processor Module ( Both Ethernet Port for simultaneous communication with Control Centre SCADA over IEC60870-5-104 Protocol and IEDs in the Substation over IEC61850 and Modbus TCP Protocol), 4 Nos. Redeundant RS 485 ports/Processor Module for communication with serial devices over IEC60870-5-103, MODBUS (Serial) and IEC 60870-5-101 protocol with the RTU. Power supply: Redundant 18-72 VDC (24 V/48 V DC) Power Supply with Diode Oring unit and MCBs with add-on NO contact SPD: 4 Nos. SPD for RS485 Ports & 4 Nos. SPD for Ethernet port Protocols : IEC 60870-5-104, IEC 61850 (ED1, ED2), IEC 60870-5-101, IEC60870-5-103, MODBUS (Serial & TCP/IP), SNMP (V1.0, V2.0, V3.0), RSTP, NTP & SNTP, Software Licenses: RTU OS, Application Software, Configuration tools, Diagnostic tools. Logic building Application-Interlock logic, Calculation Package, SMS Utility Software Application Software Licenses with minimum 10000 Data Points, 25 IEDs - IEC61850 (ED1, ED2), 20 IEDs - Serial Protocol, RTU shall Communicate to Eight Independent Remote SCADA Master on IEC 60870-5-104 Mounting: To be supplied with prewired panel (Rittal/Siemens or equivalent, size : 2315 (H) mm x 800(W) mm x 800(D) mm, both side opening), IP Class : IP54/55. Other Accessories: Interface Modules, Pre-fabricated cables for I/O modules, Auxiliaries Relays for Power Supply monitoring, MCBs for all type of Power Supplies, Networking accessories: All required networking accessories like Patch cords (UTP as per the Ethernet Switch Configuration) of suitable length, Conduits for all non-armored cables, RJ45 connectors, I/O boxes with Quad face plate and connectors etc. | EA | 1 Nos. | 0 | 23 | 75 | 98 |  | 18% | 0 | 0 | 0
2 | Without Panel | RTU without Panel I/O Requirement: with 16 DI, 8 DO, 4 AI with Auxiliary relay for each Digital Input & Output Communication Ports per RTU :2x Redundant Ethernet ports; 2 Nos. Ethernet ports/Processor Module ( Both Ethernet Port for simultaneous communication with Control Centre SCADA over IEC60870-5-104 Protocol and IEDs in the Substation over IEC61850 and Modbus TCP Protocol), 4 Nos. Redeundant RS 485 ports/Processor Module for communication with serial devices over IEC60870-5-103, MODBUS (Serial) and IEC 60870-5-101 protocol with the RTU. Power supply: Redundant 18-72 VDC (24 V/48 V DC) Power Supply and Diode Oring unit and MCBs with add-on NO contact SPD: 4 Nos. SPD for RS485 Ports & 4 Nos. SPD for Ethernet port Protocols : IEC 60870-5-104, IEC 61850 (ED1, ED2), IEC 60870-5-101, IEC60870-5-103, MODBUS (Serial & TCP/IP), SNMP (V1.0, V2.0, V3.0), RSTP, NTP & SNTP, Software Licenses: RTU OS, Application Software, Configuration tools, Diagnostic tools. Logic building Application-Interlock logic, Calculation Package, SMS Utility Software Application Software Licenses with minimum 5000 Data Points, 25 IEDs - IEC61850 (ED1, ED2), 20 IEDs - Serial Protocol, RTU shall Communicate to Eight Independent Remote SCADA Master on IEC 60870-5-104 Mounting: In existing RTU Panel size : 2315 (H) mm x 800(W) mm x 800(D) mm, both side opening), IP Class : IP54/55. Other Accessories: Interface Modules, Pre-fabricated cables for I/O modules, Auxiliaries Relays for Power Supply monitoring, MCBs for all type of Power Supplies, Networking accessories: All required networking accessories like Patch cords (UTP as per the Ethernet Switch Configuration) of suitable length, Conduits for all non-armored cables, RJ45 connectors, I/O boxes with Quad face plate and connectors etc. | No. / Substation | 1 Nos. | 50 | 50 | 0 | 100 |  |  | 0 | 0 | 0
3 | Managed Layer2 Ethernet Switch (RTU Panel) | Managed L2 Ethernet Switch for IED Communication & for SCADA Integration Communication Ports: 16 PORT (Copper ports) 10/100 MBPS Power Supply: Input power supply 18-72 (24/48)VDC Supply Redundant and MCBs with add-on NO contact Mounting Arrangement: Din Rail Mounted Option preferred Preferred Make: Ruggedcom/Hirschman/MOXA/Siemens Software: Software for Local and Remote configuration of Ethernet Switches - Enabling Monitoring, Configuration, Maintenance and backup of configuration files Shall support: 802.1Q VLAN, 802.2p, 802.1d STP, 802.3ad (Port/Link aggregation), 802.1w RSTP, 802.1s MSTP, 802.3ad LACP, IEEE 802.1ab Link Layer Disscovery Protocol and also suitable for Ring Configuration, IEEE 1613 compliance, IEC 61850, MODBUS, Ethernet/IP Compliance, IEEE1588 V2, Suitable for PRP/HSR architecture,Web-based, Telnet & Command Line Interface (CLI) for quickly configuring major managed functions, SNMPv1/v2c/v3 for different levels of network management, SNTP. Higher MTBF minimum 300000 Hours Note: TPCODL has reserved the right to procure Ethernet swicth against a different tender and may provide Ethernet Switch to the RTU vendor as a free issue. | Nos. | 2 Nos. | 100 | 238 | 150 | 488 |  | 18% | 0 | 0 | 0
4 | CMR with Mounting Base for Digital Inputs | Contact Multiplier Relay with Mounting Base: 1. Contact Material : Silver Alloy 2. Contact Rating : 5 Amps. @ 24 V/48 V DC 3. Contact Resistance : 50 Mohms max. (Initial) 4. Dielectric Strength : i) Between open contacts : 500 V RMS ii) Between Contact and Coil : 2000 V VAC 5. Insulation Resistance : 200 Mohms @ 500 V DC, 250 C 6. Operate time at Nominal Voltage : 20 milli seconds 7. Release time at nominal Voltage : 10 milli seconds 8. Ambient temperature : -40ºC to +70ºC 9. Life expectancy : i) Mechanical : 20 million DC Relay ii) Electrical : More than 100,000 Operations 10. Coil Resistance at Nominal Voltage (DC) : 30,000 Ohms +10% at 250ºC 11. Type of Contact Multiplier : 2 NO with LED Indicator + Free wheeling Diode 12. Type of mounting : DIN RAIL MOUNTING WITH SOCKET 13. No. of Poles : 2 NO 14. Other Accessories: Necessary TB, Din rail channel and other accessories to mount in CRP | No | 4 | 200 | 476 | 0 | 676 |  | 18% | 0 | 0 | 0
5 | Interposing Relay for Digital Output | Interposing Relay with Mounting Base for Digital Output 1. Auxiliary Power. : 24 V / 48 V DC 2. Input signal from field : 24 V / 48 V DC 3. Input impedance : More than 50 Kohms 4. Output signal of the RTU : 24 V / 48 V DC 5. Contact mechanism : Self Reset 6. Contact Make & Carry : 30 A for 3 Sec. & 5A continuously at 660V 7. Number of Contacts : 2 NO with LED Indicator + Free wheeling 8. Operating time : Less than 15 msec. 9. Other Accessories: Necessary TB, Din rail channel and other accessories to mount in RTU/CRP Panel 10. RTU remote rebooting over SMS | No. | 4 | 200 | 476 | 150 | 826 |  | 18% | 0 | 0 | 0
6 | Instrumentation Cable 12 C X 0.5 mm2, Armored cable for Status and Indications | Instrumentation Cable for Status and Indications 12 C X 0.5 mm2, Armored, 1100 V Rated, Annealed Stranded Copper, PVC insulated, Overall shielded field cable Preferred Make: CCI / FINOLEX / HAVELLS / Universal Cables / Incab / Asian Cable / KEI / Polycab / Ruchika | M | 50 | 2500 | 5950 | 0 | 8450 |  | 18% | 0 | 0 | 0
7 | Instrumentation Cable 7 C X 1.5 mm2, Armored for Control Output | Instrumentation Cable for Control Output 7 C X 1.5 mm2. Armored, 1100 V Rated, Annealed Stranded Copper, PVC insulated, Overall shielded field cable Preferred Make: CCI / FORT GLOSTER / FINOLEX / HAVELLS / Indian aluminum Cables / Universal Cables / Incab / Asian Cable / KEI / Polycab / Ruchika | M | 50 | 2500 | 5950 | 0 | 8450 |  | 18% | 0 | 0 | 0
8 | Twisted Pair Shielded & Over all shielded Instrumentation Cable 5 P X 1.0 mm2, Armored for Analog Input | Twisted paired Shielded & Overall Shielded Cable for Analog Inputs 5 P X 1.0 mm2, Armored, Copper twisted paired and Overall shielded cable for Analog inputs from CRP/Field panel to the RTU panel Preferred Make: CCI / FORT GLOSTER / FINOLEX / HAVELLS / Indian aluminum Cables / Universal Cables / Incab / Asian Cable / KEI / Polycab / Ruchika | M | 50 | 2500 | 5950 | 0 | 8450 |  | 18% | 0 | 0 | 0
9 | 4 C X 2.5 mm2 Copper cable for extension of CT & PT | Control Cable for CT & PT Extension 4 C X 2.5 mm2, multistrand copper cable for extending CT & CVT inputs to the MFM in the CRP panel. Preferred Make: CCI / FORT GLOSTER / FINOLEX / HAVELLS / Indian aluminum Cables / Universal Cables / Incab / Asian Cable / KEI / Polycab / Ruchika/Prime | M | 60 | 3000 | 7140 | 0 | 10140 |  | 18% | 0 | 0 | 0
10 | 2 C X 4 mm2 Cable for DC Power Supply | Power Supply Cable from DCDB to RTU Panel 2 C X 4 mm2, Armored Multistrand Power Supply cable for extending Power Supply from DCDB to RTU Panel Preferred Make: CCI / FORT GLOSTER / FINOLEX / HAVELLS / Indian aluminum Cables / Universal Cables / Incab / Asian Cable / KEI / Polycab / Ruchika | M | 100 | 5000 | 11900 | 3750 | 20650 |  | 18% | 0 | 0 | 0
11 | 2 C X 4 mm2 Cable for AC Power Supply | Power Supply Cable from DCDB to RTU Panel 2 C X 4 mm2, Armored Multistrand Power Supply cable for extending Power Supply from DCDB to RTU Panel Preferred Make: CCI / FORT GLOSTER / FINOLEX / HAVELLS / Indian aluminum Cables / Universal Cables / Incab / Asian Cable / KEI / Polycab / Ruchika | M | 100 | 15000 | 31100 | 3750 | 49850 |  | 18% | 0 | 0 | 0
12 | 4P X 0.36 mm2, Armored Communication Cable for MFM, Battery Charger, OTI/WTI, FDS, Weather sensor | Communication Cable: 4 P X 0.36 mm2 Armored multistrand Pair and Overall shielded, for Multifunction Meter looping. Preferred Make : Belden/LAPP/SATYAM/KEC/Digisol/Polycab/Parashield | M | 100 | 5000 | 11900 | 7500 | 24400 |  | 18% | 0 | 0 | 0
13 | Armored CAT6 UTP Cable | Armored CAT6 UTP Cable Preferred Make : Systemax/Finolex/Polycab/Digisol | M | 100 | 5000 | 11900 | 21500 | 38400 |  | 18% | 0 | 0 | 0
14 | Un-Armored CAT6 UTP Cable | Un-Armored CAT6 UTP Cable Preferred Make : Systemax/Finolex/Polycab/Digisol | M | 200 | 30000 | 71400 | 7500 | 108900 |  | 18% | 0 | 0 | 0
15 | Earthing and Earth Pit | Earthing: a) Earth Pit: Separate Earth Pits should be provisioned for attaining the resistance value of maximum 2 Ohms. b) Earthing Wires: RTU Panels, SIC Panel are to be wired with Earth Pit. Copper wires size should be minimum of 10 Sq.mm. (Green) Services for Earthing & Earth Pit Installation and Commissioning of Earth Pit and laying and termination of earthing cable for RTU and DC System | SET | 1 | 50 | 119 | 75 | 244 |  | 18% | 0 | 0 | 0
16 | Engineering Configuration Laptop | Configuration Laptop Hardware: Laptop with latest processor, 1 TB SSD, 8 GB RAM, DVD RW, Ethernet Port, 4 USB Ports, 1 HDMI Port, 15" Display with 1 No. Serial to USB converter Software License: Microsoft Windows compatible with latest version of configuration software, Microsoft Office License pack, Antivirus Symantec Endpoint protection small business edition with three year subscription, Configuration & Maintenance Software tools, Diagnostic tools. Logic building Application of RTU and Protection IEDs, Simulation Software, Applicable Software licenses for SIC System and shall be in-line with RTU Software. Proposed Licenses shall be independent of Engineering Configuration Laptop Hardware. | No |  | 1 | 1 | 1 | 3 |  | 18% | 0 | 0 | 0
17 | Multi Function Meter | Multi Function Meter: Requirement : For all 33kV Lines, Multifunctional 3-phase Power meter, four quadrant active and reactive energy polyphase static meter CT Type: Ring CT/Conventional Form Factor: 96 X 96 mm Accuracy Class: 0.2S/0.5S as per IEC62053:11, IEC62053:21, IEC62053-22, IEC62053-23, EC62053-31, IEC61010, IS13779, IS14697, Voltage Inputs: Operating range : 690 V AC line-to-line, 460 V AC line-to-neutral,690 V AC line-to-line, 460 V AC line-to-neutral, 57.7 V (100V) - 240 V (415 V) AC 3 phase 4 wire (3 phase 3 wire) Current Inputs: 1A / 5A (User selectable CT secondary 1A / 5A, PT Secondary) Wiring configurations: 3OP2, 4LN3, 3DIR2, 4LL3, 3OP3, 3LN3, 3LL3, 3BLN3, 3BLL3 (All wiring configurations selected via the front panel) Communication Port: RS 485 Serial Port with removable connector Protocols: MODBUS RTU, Assignable Register map, Device Address (User Configurable - (1-247)) Auxiliary Supply: 24 V / 48 V DC Other Accessories: Necessary TB, Din rail channel and other accessories for flash mounting in CRP Preferred Make: SATEC/Equivalent Services for MFM: Installation and Commissioning of Multifunction Meters in CRP Panel and its integration with RTU with required configuration for Control Centre communication over IEC-104 | No | 1 | 50 | 50 | 0 | 100 |  | 18% | 0 | 0 | 0
18 | Modem | As per specification | No |  | 0 | 0 | 75 | 75 |  | 18% | 0 | 0 | 0
| Total Amount- All Inclusive (Rs.)- Supply Items | [11 empty] | 0
B | Services
1 | Services of RTU Panel, Communication and Other Supplied System | Integration and Commissioning RTU System a) Site Survey, Design, Engineering, Finalization of BOM, FDS b) Transportation, Delivery, Unloading and Storage c) Installation and Commissioning of Pre-wired RTU Panel, Networking equipment & other Accessories d) Minor Civil Activities for Installation of RTU panel e) Cable laying, termination and continuity check of all cables (Instrumentation, Communication & Power cables) f) Integration of all Protection, MFM, Condition Monitoring Devices etc. g) Powering up of all supplied materials h) Configuration of RTU and its accessories i) I/O testing, Pre- SAT testing of Hardware and Software functionality j) Integrated FAT & SAT for Hardware and Software k) Integrated testing with Purchaser's SCADA System l) Demonstration of System Capacity and Performance Guarantee Test m) Submission of As-Built Drawings, RTU Backup | EA | 1 | 0 | 69 | 75 | 144 |  | 18% | 0 | 0 | 0
2 | Services of RTU , Communication and Other Supplied System | Integration and Commissioning RTU System a) Site Survey, Design, Engineering, Finalization of BOM, FDS b) Transportation, Delivery, Unloading and Storage c) Installation and Commissioning of Pre-wired RTU Rack, Networking equipment & other Accessories d) Minor Activities for Installation of RTU Rack in the Existing Panel e) Cable laying, termination and continuity check of all cables (Instrumentation, Communication & Power cables) f) Integration of all Protection, MFM, Condition Monitoring Devices etc. g) Powering up of all supplied materials h) Configuration of RTU and its accessories i) I/O testing, Pre- SAT testing of Hardware and Software functionality j) Integrated FAT & SAT for Hardware and Software k) Integrated testing with Purchaser's SCADA System l) Demonstration of System Capacity and Performance Guarantee Test m) Submission of As-Built Drawings, RTU Backup | EA | 1 | 50 | 50 | 0 | 100 |  | 18% | 0 | 0 | 0
3 | Warranty | Warranty Services for the Bidder's owned & Sub-Vendors supplied Hardware, Software, Up-gradation & Patch Management of Software during the Standard warranty period of 5 Years from the date of system handover after SAT, resolution of all punch point of SAT and trouble-free operation of the entire system for a period of one month. | Lumpsum |  | 1 | 1 | 1 | 3 |  | 18% | 0 | 0 | 0
4 | TrainingTraining (10 Man-days of Trainer) | On-site Training on Supplied equipment and Application Software | Trainer Man-days |  |  |  |  | Included with Complete Scope of Work
5 | Cyber Security Audit | Cyber Security Audit by third party auditor empaneled information security auditing organization by CERT-In | Nos. |  | 1 | 1 | 1 | 3 |  | 18% | 0 | 0 | 0
| Total Amount- All Inclusive (Rs.)- Services | [11 empty] | 0
| Total Amount- All Inclusive (Rs.)- Supply +Services | [11 empty] | 0
C | Mandatory Spares
i | Unit Cost to be utilised for addition/ deletion of quantity as per site requirement | RTU Chassis | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
ii |  | CPU Module ( along with licensed SD card if applicable) of the RTU | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
iii |  | Power Supply Module of the RTU | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
iv |  | Communication Module( along with licensed SD card if applicable) (Ethernet) | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
v |  | Communication Module( along with licensed SD card if applicable) (Serial) | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
vi |  | DI Cards with Interface Module & Cables for Digital Inputs | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
vii |  | DO Cards with Interface Module & Cables for Digital Output | Sets |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
viii |  | AI Cards with Interface Module & Cables for Analog Inputs | Sets |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
ix |  | Any Other Modules Specific to OEM Solution | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
x |  | Managed Ethernet Switch – as per proposed solution | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
xi |  | Managed L2 Ethernet Switch for IED Communication & for SCADA Integration Communication Ports: 08 PORT (Copper ports) 10/100 MBPS Power Supply: Input power supply 18-72 (24/48)VDC Supply and MCBs with add-on NO contact Mounting Arrangement: Din Rail Mounted Option preferred Preferred Make: Ruggedcom/Hirschman/MOXA/Siemens Software: Software for Local and Remote configuration of Ethernet Switches - Enabling Monitoring, Configuration, Maintenance and backup of configuration files Shall support: 802.1Q VLAN, 802.2p, 802.1d STP, 802.3ad (Port/Link aggregation), 802.1w RSTP, 802.1s MSTP, 802.3ad LACP, IEEE 802.1ab Link Layer Disscovery Protocol and also suitable for Ring Configuration, IEEE 1613 compliance, IEC 61850, MODBUS, Ethernet/IP Compliance, IEEE1588 V2, Suitable for PRP/HSR architecture,Web-based, Telnet & Command Line Interface (CLI) for quickly configuring major managed functions, SNMPv1/v2c/v3 for different levels of network management, SNTP. Higher MTBF minimum 300000 Hours Note: TPCODL has reserved the right to procure Ethernet swicth against a different tender and may provide Ethernet Switch to the RTU vendor as a free issue. | No. |  | - |  |  | 1
xii |  | CMR Relay with Base as per proposed solution | Lot |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
xiii |  | HDR Relay with Base as per proposed solution | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
xiv |  | Diode OR-ing Unit (If Applicable) | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
xv |  | RTU Rack without panel as per Proposed Solution with all CPU & Communication Modules, Application s/w, licenses, accessories, cables etc. | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
xvi |  | Fluke 362 Clamp Meter 200A AC/DC Clamp Meter | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
xvii |  | RISHABH AET 23 Smart Digital Earth Tester | No. |  | - |  |  | 1 |  | 18% | 0 | 0 | 0
| Total items- All Inclusive (Rs.)- Spares | [11 empty] | 0

## BCPU (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Sl. No. | Item | Description | UOM | HSN/SAC Code | Qty/ PSS | Total Required Quantity (A) | Unit Rate (B) | GST (%) | GST (INR) (C) | Gross Unit Rate (D=B+C) | Gross Price (E=A*D)
|  | Nos. of 33/11 kV Primary Substations | 92
A | Pre-Wired RTU Panel
1 | 33kV BCPU | 33kV BCPU 301002394 Internal modular in design. The device shall be flush mounted type with draw out design . All PCB used in relays should have harsh environmental coating as per standard IEC 60068 (HEC) to increase the particle repellency. Enclosure protection shall be IP54 from front and IP 20 from rear Fascia: The fascia of the IED should have a clear and bright LCD display. Inputs & Outputs: The auxiliary input circuit shall be protected by surge protecti The auxiliary input/output should be suitable for both 24V and 48V DC Digital Inputs : 20 Digital Output: 8 CT Inputs: 4 PT Inputs: 4 Protection Function: O/C , E/F, U/V & O/V, Broken conductor,High impedance protection, VT supervision CT supervision, Every protection function should have blocking facility I2T feature to monitor breaker wear and tear Monitoring: Fault current (Analogue value, same to be mapped at SCADA for all 4 channels) Auto reclose Communication Ports: 2x RJ45 Ethernet port compliant to IEC 61850 (Ed.1 &2) and RSTP. USB for configuration Protocol: IEC61850 Ed1 & 2, SNTP, RSTP, SNMP ( latest version) Time Synchronization: SNTP support 4 Nos. SNTP Server, Standard diagnostic features. Oscillography files System Events: 3300 Events minimum & Time resolution of 1ms Configuration Software: 2x | Nos. |  | 2 | 184 |  | 18% | 0 | 0 | 0
2 | 11kV BCPU | 11kV BCPU 301002394 Internal modular in design. The device shall be flush mounted type with draw out design . All PCB used in relays should have harsh environmental coating as per standard IEC 60068 (HEC) to increase the particle repellency. Enclosure protection shall be IP54 from front and IP 20 from rear Fascia: The fascia of the IED should have a clear and bright LCD display. Inputs & Outputs: The auxiliary input circuit shall be protected by surge protecti The auxiliary input/output should be suitable for both 24V and 48V DC Digital Inputs : 16 Digital Output: 10 CT Inputs: 4 PT Inputs: 4 Protection Function: O/C , E/F, U/V & O/V, Broken conductor,High impedance protection, VT supervision CT supervision, Every protection function should have blocking facility I2T feature to monitor breaker wear and tear Monitoring: Fault current (Analogue value, same to be mapped at SCADA for all 4 channels) Auto reclose Communication Ports: 2x RJ45 Ethernet port compliant to IEC 61850 (Ed.1 &2) and RSTP. USB for configuration Protocol: IEC61850 Ed1 & 2, SNTP, RSTP, SNMP ( latest version) Time Synchronization: SNTP support 4 Nos. SNTP Server, Standard diagnostic features. Oscillography files System Events: 3300 Events minimum & Time resolution of 1ms Configuration Software: 2x | Nos. / RTU |  | 3 | 276 |  | 18% | 0 | 0 | 0
4 | Master trip relay (86) | The relay shall be electrical and hand reset type having operating time not more than 12 ms. The relay should be flush mounting type and having minimum 6 NO and 2 NC contacts shall be suitable to operate in both 24 V and 48 V DC system. The master trip relay should have ring type interface for wiring termination. Preference Make & Model 18-02-2023 GE make MVAJM model(or as per specification) | Nos./ Substation |  | 6 | 552 |  | 18% | 0 | 0 | 0
5 | L/R Switch | L/R key (2NO+2NC) | Meters/ Substation |  | 6 | 552 |  | 18% | 0 | 0 | 0
5 | TNC Switch | TNC key (4NO+4NC). | Meters/ Substation |  | 6 | 552 |  | 18% | 0 | 0 | 0
Sub Total | [10 empty] | 0
K | Services for BCPU Commissioning
1 | Services of BCPU Commissioning | Integration and Commissioning BCPU System a) Site Survey, Design, Engineering, Finalization of BOM, FDS b) Transportation, Delivery, Unloading and Storage c) Installation and Commissioning of BCPU, Networking equipment & other Accessories d) Minor Civil Activities for Installation of BCPU e) Cable laying, termination and continuity check of all cables (Instrumentation, Communication & Power cables) f) Configuration of BCPUand its accessories g) I/O testing, Pre- SAT testing of Hardware and Software functionality h) Integrated FAT & SAT for Hardware and Software i) Integrated testing with Purchaser's SCADA System j) Demonstration of System Capacity and Performance Guarantee Test k) Submission of As-Built Drawings, RTU Backup | Lumpsum / Substation |  | 5 | 460 |  | 18% | 0 | 0 | 0
Total of Services (K) | [8 empty] | 0 | 0 | 0 | 0
Grand Total of Supply + Services
L | Standard Warranty | Standard Warranty
1 |  | Warranty Services for the Bidder's owned & Sub-Vendors supplied Hardware, Software, Up-gradation & Patch Management of Software during the Standard warranty period of 5 Years from the date of system handover after SAT, resolution of all punch point of SAT and trouble-free operation of the entire system for a period of one month. | Lumpsum |  |  | 1 |  | 18% | 0 | 0 | 0
Total of Standard Warranty | [10 empty] | 0
M | Training | Training (20 Man-days of Trainer)
1 |  | On-site Training on Supplied equipment and Application Software | Man-days |  |  | 20 |  | 18% | 0 | 0 | 0
Total of Training | [10 empty] | 0
Grand Total of Supply + Services+Standard Warranty + Trainning | [10 empty] | #REF!
2862857

## Mandatory Spares (hidden)
1 | 2 | 3 | 4 | 5 | 7 | 8 | 9 | 10 | 11 | 12
Sl. No. | Item | Description | UOM | HSN/SAC Code | Total Required Quantity (A) | Unit Rate (B) | GST (%) | GST (INR) (C) | Gross Unit Rate (D=B+C) | Gross Price (E=A*D)
A | Spares | Mandatory Spares
A.1 |  | RTU Rack without panel as per Proposed Solution with all Application s/w, licenses, accessories, cables etc. | Sets |  | 5 |  |  | 0 | 0 | 0
A.2 |  | RTU Chassis | Nos. |  | 5 |  |  | 0 | 0 | 0
A.3 |  | CPU Module ( along with licensed SD card if applicable) of the RTU | Nos. |  | 10 |  |  | 0 | 0 | 0
A.4 |  | Power Supply Module of the RTU | Nos. |  | 10 |  |  | 0 | 0 | 0
A.5 |  | Communication Module( along with licensed SD card if applicable) (Ethernet) | Nos. |  | 10 |  |  | 0 | 0 | 0
A.6 |  | Communication Module( along with licensed SD card if applicable) (Serial) | Sets |  | 5 |  |  | 0 | 0 | 0
A.7 |  | DI Cards with Interface Module & Cables for Digital Inputs | Sets |  | 10 |  |  | 0 | 0 | 0
A.8 |  | DO Cards with Interface Module & Cables for Digital Output | Sets |  | 5 |  |  | 0 | 0 | 0
A.9 |  | AI Cards with Interface Module & Cables for Analog Inputs | Sets |  | 5 |  |  | 0 | 0 | 0
A.10 |  | Any Other Modules Specific to OEM Solution | Nos. |  | 2 |  |  | 0 | 0 | 0
A.11 |  | Managed Ethernet Switch – as per proposed solution | Nos. |  | 10 |  |  | 0 | 0 | 0
A.12 |  | CMR Relay with Base as per proposed solution | Nos. |  | 10 |  |  | 0 | 0 | 0
A.13 |  | HDR Relay with Base as per proposed solution | Nos. |  | 10 |  |  | 0 | 0 | 0
A.14 |  | Diode OR-ing Unit (If Applicable) | Nos. |  | 2 |  |  | 0 | 0 | 0
A.15 |  | Fluke 362 Clamp Meter 200A AC/DC Clamp Meter | Nos. |  | 7 |  |  | 0 | 0 | 0
A.16 |  | RISHABH AET 23 Smart Digital Earth Tester | Nos. |  | 2 |  |  | 0 | 0 | 0
Total of Spares (A)