## Sheet1
GENERAL TECHNICAL PARTICULARS
SL. NO. | TECHNICAL PARTICULARS | DESIRED VALUE |  | Offered by Bidder (Confirmed /mention deviation if any)
1 | Rating of AB Switch | 400 Amps AB Switch | 200 Amps AB Switch
2 | Reference standards (latest amend.) | IS 9920, IEC 129, IEC 62231 with up-to-date amendments, IS 1239 , IEC 61109 with up-to-date amendments
3 | Installation | Outdoor | Outdoor
4 | Suitable for Mounting | Horizontal Rotating Type
5 | Type | 3 Pole
6 | Service Voltage | 11 kV
7 | Rated Voltage | 12 kV
8 | Rated Frequency | 50 Hz
9 | Current Carrying Capacity | 400 Amps | 200 Amps
10 | Rated short time current | 16 kA for 1sec
11 | Rated peak withstand current | 40 kA
12 | Rated main active load breaking capacity | 10 Amp
13 | Rated line charging breaking capacity | 2.5A
14 | Rated Cable charging breaking capacity | 10A
15 | Rated Transformer off load breaking Capacity | 6.3A
16 | One minute power frequency with stand voltage Dry | 35kV RMS
17 | One minute power frequency withstand voltage Wet | 35kV RMS
18 | Dry flashover Voltage | 55kV
19 | Power Frequency puncture withstand voltage | 1.3 times of actual dry flashover Voltage
20 | Visible Discharge Voltage | 9kV RMS
21 | 1 Minute Power Frequency withstand voltage between pole and earth | 28kV RMS
22 | 1 Minute Power frequency withstand across the isolation distance | 32kV RMS
23 | Impulse with stand voltage for positive and negative polarity (1.2 / 50) micro second wave)
a | Across Isolating distance | 85kV Peak
b | To earth and between poles | 75kV Peak
24 | No. of Post Per Pole (The percentage of silicon content on the polymeric post insulator should be above 40%) | 2
25 | Total No. of post | 6
25. a | Make of Insulator | Sun Kouture / Scenario / Prithvi Industries / Yamuna Power/ Jainco Transmission/ Navitas Insulators/ Deccan Electricals
Complete type test reports of insulator to be provided during tender evaluation process.
Year of manufacturing to be properly engraved on the insulator.
25. b | Minimum Creepage Distance | 320 mm
25. c | FRP Dia. of the Post Insulator (min.) Negative tolerance not allowed | 24mm
25. d | Dai of Weather sheds | >100mm
25. e | Thickness of Housing (min) | 3mm
25. f | PCD of Insulator | 57mm
25. g | Type of Sheds | Aerodynamic
25. h | Phase to Phase Clearance | 760mm
25. i | Isolation Distance in switch open condition | 380mm
25. j | Vertical clearance from Top of insulator | 254mm (min)
26 | Copper contacts Temp in Air should not exceed | 65 Degree C
27 | Fixed & Moving Contact Material | Electrolytic Copper Grade (Min 99.9% Cu) silver plating of 15 Microns thickness
28 | Size of fixed contacts (Copper Type | 80mmx50mmx8mm | 70mmx35mmx6mm
| Electrolytic with silver plated) | (50x8x2 Fingers) | (35x6x2 Finger)
29 | Fixed Contacts assembly | Fixed contact controlled by phosphorus stainless-steel high-pressure spring housed in robust Steel Cover. It is essential that provision shall be made in fixed female contacts to take the shock arising from the closing of moving contact blade without the same being transmitted to the post insulator.
30 | Size of Moving contacts (Copper Type Electrolytic with silver plated) (coating thickness not less than 10 microns) | 220mmx50mmx8mm | 220mmx35mmx6mm
31 | Moving Contacts assembly | The switch shall have such a spring mechanism so as to ensure that the speed of the opening of contact is independent of speed of manual operation.
32 | Moving Contact supporting Angle | 50mmx50mmx5mm | 45mmx45mmx5mm
33 | Size of rods used for arcing horns | 10 mm
34 | Insulation for tinned Copper braid/rope | Polyolefin, (RSFR-H) type
35 | Copper Flexible BRAIDED Tape - 320mm Long, Tined plated with | 450gm / Mtr
| Brass Nut, bolt & Washers | M12 Brass Nut, bolt & Washers
36 | Minimum size*Length of Coupling Hot Dip GI Solid Pipe for Phase coupling pipe, B Class ( Nominal Bore) | MS HDG
25 NB, 1800mm long for 3 Pole (as per IS
1239)
Class: Medium
OD (max): 34.2mm and (min): 33.3mm
Thickness: 3.2mm
Tolerance: +/-10% on thickness
Make: Jindal
37 | Operating Down Pipe, B class (IS 1239) (Nominal bore) | MS HDG
32 NB, 7Mtr Long (Without Wielding/joints) as per IS 1239
Class: Medium
OD (max): 42.9 mm and (min): 42.0 mm
Thickness: 3.2mm
Tolerance: +/-10% on thickness
Make: Jindal
38 | Temperature Rise Limit (w.r.t ambient temp)
| - Tinned Copper contacts | 65°C
| - Terminals | 65°C
| - Metal Parts | 40°C
39 | Bearings | 4 nos. self-lubricating bearing to be provided with grease nipple including 4th bearing being a thrust bearing. (Bearing make shall be SKF/ FAG)
40 | Locking arrangement (LOTO) | Provision for pad locking at both ‘ON’ & ‘OFF’ Position
LOTO arrangement lock required
41 | Earth Terminal | M12 Bolts with nuts and flat washer shall be provided at base channel as earthing Terminal.
42 | ‘T’ Connection | The T connection provided on the channel having ‘Moving contact’ shall be G.I Nut & bolt at the bottom end to facilitate replacement of this unit only during requirements & avoid entire change of arm.
43 | ‘I’ bolt | 2 Nos of ‘I’ Bolt for down operating pipe to be provided. Threaded portion shall be 75mm.
M12 Dia, Double nuts for each ‘I’ bolt to be provided.
44 | Mounting Channel HDG 100 microns | 75x40x4.8 mm hot dip galvanized channel length
480 mm min. (C/C slotted hole 18x 36 mm- 250mm)
Zinc coating thickness: Min 100 Microns
(Make- TATA/ SAIL/ JINDAL/ RINL)
45 | Moving & Fixed Terminals | Terminal connectors for both movable and fixed should be of copper flats with 2 no. of 10 mm dia holes provided with suitable brass bolts, double nuts, washers & spring washers
Electrolytic copper (Min 99.9% Cu) with silver plating of 15 microns thickness
46 | Min Cross sectional Dimension of Fixed Terminal | 80 x 50 x 8 mm | 70 X 35 X 6 mm
47 | Min Cross sectional Dimension of Moving Terminal | 80 x 50 x 8 mm | 70 X 35 X 6mm
48 | Socket | One number solder less bimetallic socket (Electrolytic Copper tin plated) for each connector suitable sockets for each connector suitable up to 55- 100 mm² AAA conductor.
One no. of 12 mm dia. brass bolts, double nuts, plain washers & spring washers to be provided for socket.
49 | Pressure Spring | Stainless steel
50 | Nuts, Bolts & Washers | For current carrying parts: Brass
For non-current carrying parts: SS 316 nuts & bolts
51 | Marking/Engraving (Parameters should be embossed on Aluminium Sheet of thickness 0.4 mm with black background. It should be riveted on MS channel of AB switch) per each phase | 1. Rated Voltage
2. Manufacturer Name
3. Month/Year of Manufacture
4. Serial No.
5. PO No.
6. Rated Normal Current in Amps
7. Rated One Second Short-Time Current
8. Property of TPCODL/ TPNODL/ TPWODL/ TPSODL