## Sheet1
GENERAL TECHNICAL PARTICULARS
SL. NO. | TECHNICAL PARTICULARS | TP Odisha DISCOMs TS Requirements |  |  |  | Offered by Bidder (Confirmed /mention deviation if any)
1 | Rating of Vertical AB Switch | 400 Amp | 200 Amp |  | 200 Amp
2 | Installation | Outdoor
3 | Type | 3 Pole | 3 Pole |  | 2 Pole
4 | Service Voltage | 12 kV
5 | Rated Voltage | 11 kV
6 | Rated Frequency | 50 Hz
7 | Current Carrying Capacity | 400 Amp | 200 Amp |  | 200 Amp
8 | Rated short time current | 16 kA for 1sec
9 | Rated peak withstands current | 40 kA
10 | Rated main active load breaking capacity | 10 Amp
11 | Rated off-loads breaking capacity | 6.3 A
12 | Power Frequency withstand voltage | 28kV
between pole and earth
13 | Power frequency withstand voltage across | 32kV
the isolation distance
14 | No. of Post Per Phase | 3
15 | Total No. of post (Polymer) | 9 | 9 |  | 6
16 | Minimum Creepage Distance | 320 mm
16.a | FRP Dia. of the Post Insulator (min.) | 24mm
16.b | Dai of Weather sheds | >100mm
16.c | Thickness of Housing (min) | 3mm
16.d | Type of Sheds | Aerodynamic
16.f | Manufacturing year of insulator | To be engraved on insulator
16.g | PCD | 57 mm
17 | Make of Insulator | Sun Kouture / Scenario / Prithvi Industries / Yamuna Power/ Jainco Transmission/ Navitas Insulators/ Deccan Electricals
Complete type test reports of insulator to be provided during tender evaluation process.
Year of manufacturing to be properly engraved on the Insulator.
18 | Phase to Phase Clearance | 760 mm
19 | Isolation Distance | 400 mm
20 | Size of flexible tinned copper braid tape (with 1A/mm2 current density) | 400 sq.mm | 200 sq.mm |  | 200 sq.mm
|  | 35 X 5 | 25 X 5 |  | 25 X 5
21 | Minimum length of insulated tinned copper | 550 mm
Braid / rope per phase
22 | Size of fixed contacts (with 1 A/mm2 current density) | 400 sq. mm | 200 sq. mm |  | 200 sq. mm
23 | Current density of tinned Copper | 1 Amps/mm2
24 | Size of rods used for arcing horns | 10 mm
25 | Insulation for tinned Copper braid/rope | Polyolefin, (RSFR-H) type
26 | Minimum size*Length of Coupling GI Solid Rod (Operating square bar) | 25X25X1800mm | For 3 pole |  | For 2 pole
|  |  | 25X25X1800mm |  | 25X25X1200mm
27 | Minimum Thickness of GI Strip (Pentagraph) | 20mmX3mm
Temperature Rise Limit (w.r.t ambient temp)
28 | - Tinned Copper contacts | 65° C
| - Terminals | 65° C
| - Metal Parts | 40° C
29 | Fixed contact size (X2) | 50 X 8 X 80 (x2) | 35 X 6 X 70 (x2) |  | 35 X 6 X 70 (x2)
30 | Moving contact | 50 X 8 X 200 | 35 X 6 X 200 |  | 35 X 6 X 200
31 | Fixed & moving contact material | Electrolytic Copper Grade (Min 99.9% Cu) silver plating of 15 Microns thickness
32 | Gi base channel | 75X40X4.8 mm 650 mm long (Make-TATA/SAIL/JINDAL/ RINL)
33 | Fixed terminal | 50 X 8 X 90 mm | 35 X 6 X 80 mm |  | 35 X 6 X 80 mm
34 | Moving terminal | 50 X 8 X 130 mm | 35 X 6 X 130 mm |  | 35 X 6 X 130 mm
35 | Fixed & moving terminal material | Electrolytic Copper Grade (Min 99.9% Cu) silver plating of 15 Microns thickness
36 | Terminal Connector | One no. of bimetallic sockets shall be used at both ends suitable for 55-100 mm2 AAAC conductor.
One no. of 12 mm dia. brass bolts, double nuts, plain washers & spring washers to be provided for socket.
37 | Operating down pipe | MS HDG
32 NB, 6-meter-without wielding as per IS 1239
Class: Medium
OD (max): 42.9 mm and (min): 42.0 mm
Thickness: 3.2mm
Tolerance: +/-10% on thickness
Make: Jindal
38 | Locking arrangement (LOTO) | Provision for pad locking at both ‘ON’ & ‘OFF’ Position
LOTO arrangement lock required
39 | Earth terminal | M10, MS(HDG)
40 | Marking/Engraving (Parameters should be embossed on Aluminum Sheet of thickness 0.4 mm with black background. It should be riveted on MS channel of AB switch) per each phase | 1. Rated Voltage
2. Vertical
3. Manufacturer Name
4. Month/Year of Manufacture
4. Serial No.
5. PO No.
6. Rated Normal Current in Amps
7. Rated One Second Short-Time Current
8. Property of TPCODL/ TPNODL/ TPWODL/ TPSODL
41 | Arching horn size | 10 mm GI
42 | Rocker assembly | MS (HDG)
43 | Eye hook | MS HDG (8 mm), 1 No
44 | ‘I’ bolt | 2 Nos of ‘I’ Bolt for down operating pipe to be provided. Threaded portion shall be 75mm.
M12 Dia, Double nuts for each ‘I’ bolt to be provided.
45 | Spring (SS) in fixed contact assembly (Per phase) | Total no of spring 8 | Total no of spring 8 |  | Total no of spring 4
46 | Copper foil in fixed contact assembly | Yes
47 | Nut, bolt & washer | Fixed & moving connector parts |  | Brass nut, bolt & washer
|  | Other |  | GI nut, bolt & washer
48 | Silver plating thickness | 15 microns
49 | Zinc coating thickness | 100 microns