## Sheet1
GENERAL TECHNICAL PARTICULARS
SL. NO. | TECHNICAL PARTICULARS | TP Odisha DISCOMs TS Requirements | Offered by Bidder (Confirmed /mention deviation if any)
1 | Rating of AB Switch | 400 Amps AB Switch
1.a | Reference standards (latest amend.) | IS 9920, IEC 129, IEC 62231 with up-to-date amendments, IS 1239, IEC 61109 with up-to-date amendments
2 | Installation | Outdoor
3 | Suitable for Mounting | Horizontal Rotating Type
4 | Type | 3 Pole
5 | Service Voltage | 33 kV
6 | Rated Voltage | 36 kV
7 | Rated Frequency | 50 Hz
8 | Current Carrying Capacity | 400 Amps
9 | Rated short time current | 16 kA for 1sec
10 | Rated peak withstand current | 40 kA
11 | Rated Short circuit making capacity | 25 KA RMS
12 | Rated Cable Charging breaking capacity | 40 A RMS
13 | Rated line charging breaking capacity | 5.3 A RMS
14 | Rated Transformer off load breaking Capacity | 16 A RMS
15 | One-minute power frequency with stand voltage Dry | 95 KV RMS
16 | One-minute power frequency withstand voltage Wet | 75 KV RMS
17 | Power Frequency puncture withstand voltage | 1.3 times of actual dry flashover voltage
A | Visible Discharge Voltage | 27 KV RMS
B | Dry flashover Voltage | 95 kV
18 | Power Frequency withstand voltage between pole and earth | 70 KV RMS
19 | Power frequency withstand voltage across the isolation distance | 80 KV RMS
20 | Impulse with stand voltage for positive and negative polarity (1.2 / 50) micro second wave)
A | Across Isolating distance | 195 KV Peak
B | To earth and between poles | 170 KV Peak
21 | No. of Post Per Phase (Polymeric, IEC 62231) | 2
22 | Total No. of post | 6
The percentage of silicon content on the polymeric post insulator should be above 40%)
22.a | Make of Insulator | Sun Kouture / Scenario / Prithvi Industries / Yamuna Power/ Jainco Transmission/ Navitas Insulators/ Deccan Electricals
Complete type test reports of insulator to be provided during tender evaluation process.
Year of manufacturing to be properly engraved on the Insulator
22.b | FRP Dia of the Post Insulator (min) | 32mm
22.c | Dai of Weather sheds | >100mm
22.d | Thickness of Housing (min) | 3mm
22.e | PCD of Insulator | 76mm
22.f | Type of Sheds | Aerodynamic
23 | Minimum Creepage Distance | 900 mm (one post)
24 | Phase to Phase Clearance | 1200 mm
25 | Isolation Distance in switch open condition | 640 mm
26 | Vertical clearance from Top of Insulator cap to mounting channel | 508 mm (Minimum)
27 | Copper contacts Temp in Air should not exceed | 65 Degree
28 | Fixed & Moving Contact Material | Electrolytic Copper Grade (Min 99.9% Cu) silver plating of 15 Microns thickness
29 | Size of fixed contacts (Copper | 80mmx50mmx8mm
| Type Electrolytic with silver plated) (coating thickness not less than 15 microns) | Jaw assemblies are to be bolted through stainless steel flat and spring washer (Min 6 nos. of phosphor bronze high-pressure spring to be used on each post).
30 | Size of Moving contacts (Copper Type | 250mmx50mmx8mm (a Min deposit of 15 micron of Silver on copper contact)
Electrolytic with silver plated) (coating thickness not less than 15 microns)
31 | Moving Contact supporting Angle | 50mmx50mmx6mm
32 | Size of rods used for arcing horns | 10 mm
33 | Insulation for tinned Copper braid/rope | Polyolefin, (RSFR-H) type
34 | Copper Flexible BRAIDED Tape - | 450gm /Mtr
| 420 mm Long, Tined plated with Brass Nut, bolt & Washers both ends shall be crimped with copper socket through brass bolts and nuts | M12 Brass Nut, bolt & Washers
35 | Minimum size*Length of Coupling Hot Dip GI Solid Pipe for Phase coupling pipe, B Class (IS 1239) (Nominal Bore) | MS HDG
25 NB, 2500mm long for 3 Pole (as per IS
1239)
Class: Medium
OD (max): 34.2mm and (min): 33.3mm
Thickness: 3.2mm
Tolerance: +/-10% on thickness
Make: Jindal
36 | Operating Down Pipe, B Class (IS 1239) (Nominal Bore) | MS HDG
32 NB, 7Mtr Long (Without Wielding/joints) as per IS 1239
Class: Medium
OD (max): 42.9 mm and (min): 42.0 mm
Thickness: 3.2mm
Tolerance: +/-10% on thickness
Make: Jindal
37 | Temperature Rise Limit (w.r.t ambient temp)
| - Tinned Copper contacts | 65°C
| - Terminals | 65°C
| - Metal Parts | 40°C
38 | Arching Horns | 10 mm dia GI rod
39 | Locking Arrangement (LOTO) | Provision for pad locking at both ‘ON’ & ‘OFF’ position
LOTO arrangement lock required
40 | Earth Terminal | M12 Bolts with nuts and flat washer shall be provided at base channel as earthing Terminal.
41 | ‘T’ Connection | The T connection provided on the channel having ‘moving contact’ shall be G.I Nut &
bolt at the bottom end to facilitate replacement of this unit only during requirements & avoid entire change of arm.
42 | ‘I’ bolt | 2 Nos of ‘I’ Bolt for down operating pipe to be provided. Threaded portion shall be 75mm.
M12 Dia, Double nuts for each ‘I’ bolt to be provided.
43 | Supporting Channel HDG | 100x50x6 mm Hot dip galvanized channel (C/C slotted 18x36 hole 250 mm) Min. 760 mm length
Zinc coating thickness: Min 100 Microns
(Make- TATA/ SAIL/ JINDAL/ RINL)
44 | Moving & Fixed Terminals Material | Terminal connectors for both movable and fixed should be of copper flats Connectors
Electrolytic copper (Min 99.9% Cu) with silver plating of 15 microns thickness.
45 | Cross sectional Dimension of Fixed and Moving Terminal | Fixed Connector Size: 80 x 50 x 8
Moving Connector Size: (80 x50) x (80 x 50) x 8 mm with 2 no. of 14 mm dia holes provided with suitable brass bolts, double nuts, washers & spring washers
46 | SOCKET: | SOCKET: One no. of bimetallic copper sockets shall be used at both ends suitable for 100-232 sqmm AAAC conductor. One no. of 12 mm dia. brass bolts, double nuts, plain washers & spring washers to be provided for socket
47 | Bearing | 4 nos. self-lubricating bearing to be provided with grease nipple including 4th bearing being a thrust bearing. (Bearing make shall be SKF/ FAG)
48 | Pressure Spring | Stainless steel
49 | Nuts, Bolts & Washers | For current carrying parts: Brass
For non-current carrying parts: SS 316 nuts & bolts
50 | Marking/Engraving (Parameters should be embossed on Aluminium Sheet of thickness 0.4 mm with black background. It should be riveted on MS channel of AB switch) per each phase | 1. Rated Voltage
2. Manufacturer Name
3. Month/Year of Manufacture
4. Serial No.
5. PO No.
6. Rated Normal Current in Amps
7. Rated One Second Short-Time Current
8. Property of TPCODL/ TPNODL/ TPWODL/ TPSODL